## Specification
LS | SS | Length | Gage | Connector | Number of MPT | MPT Load | MPT Size | JTR Load | JTR Size | Reninforcement Class | External Reninforcement
12 | 12 | 60 | 26 | S&D | - | - | - | - | - | - | -
14 | 14 | 60 | 26 | S&D | - | - | - | - | - | - | -
16 | 16 | 60 | 26 | S&D | - | - | - | - | - | - | -
18 | 18 | 60 | 26 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
20 | 20 | 60 | 26 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
22 | 22 | 60 | 26 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
24 | 24 | 60 | 26 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
26 | 26 | 60 | 26 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
28 | 28 | 60 | 26 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
30 | 30 | 60 | 26 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
32 | 32 | 60 | 24 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
34 | 34 | 60 | 24 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
36 | 36 | 60 | 24 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
38 | 38 | 60 | 24 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
40 | 40 | 60 | 24 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
42 | 42 | 60 | 24 | T25 a/b TDC/TDF | - | - | - | - | - | - | -
44 | 44 | 60 | 24 | T25 a/b TDC/TDF | 1 | 45.0 lbs | 1/2 inch EMT | - | - | - | -
46 | 46 | 60 | 24 | T25 a/b TDC/TDF | 1 | 47.0 lbs | 1/2 inch EMT | - | - | - | -
48 | 48 | 60 | 24 | T25 a/b TDC/TDF | 1 | 49.0 lbs | 1/2 inch EMT | - | - | - | -
50 | 50 | 60 | 24 | T25 a/b TDC/TDF | 1 | 51.0 lbs | 1/2 inch EMT | - | - | - | -
52 | 52 | 60 | 24 | T25 a/b TDC/TDF | 1 | 53.0 lbs | 1/2 inch EMT | - | - | - | -
54 | 54 | 60 | 24 | T25 a/b TDC/TDF | 1 | 55.0 lbs | 1/2 inch EMT | - | - | - | -
56 | 56 | 60 | 24 | T25 a/b TDC/TDF | 1 | 57.0 lbs | 1/2 inch EMT | - | - | - | -
58 | 58 | 60 | 24 | T25 a/b TDC/TDF | 1 | 59.0 lbs | 1/2 inch EMT | - | - | - | -
60 | 60 | 60 | 24 | T25 a/b TDC/TDF | 1 | 61.0 lbs | 1/2 inch EMT | - | - | - | -
62 | 62 | 60 | 22 | T25 a/b TDC/TDF | 1 | 63.0 lbs | 1/2 inch EMT | - | - | - | -
64 | 64 | 60 | 22 | T25 a/b TDC/TDF | 1 | 65.0 lbs | 1/2 inch EMT | - | - | - | -
66 | 66 | 60 | 22 | T25 a/b TDC/TDF | 1 | 67.0 lbs | 1/2 inch EMT | - | - | - | -
68 | 68 | 60 | 22 | T25 a/b TDC/TDF | 1 | 69.0 lbs | 1/2 inch EMT | - | - | - | -
70 | 70 | 60 | 22 | T25 a/b TDC/TDF | 1 | 71.0 lbs | 1/2 inch EMT | - | - | - | -
72 | 72 | 60 | 22 | T25 a/b TDC/TDF | 1 | 73.0 lbs | 1/2 inch EMT | - | - | - | -
74 | 74 | 60 | 18 | T25 a/b TDC/TDF | 1 | 75.0 lbs | 1/2 inch EMT | - | - | - | -
76 | 76 | 60 | 18 | T25 a/b TDC/TDF | 1 | 77.0 lbs | 1/2 inch EMT | - | - | - | -
78 | 78 | 60 | 18 | T25 a/b TDC/TDF | 1 | 79.0 lbs | 1/2 inch EMT | - | - | - | -
80 | 80 | 60 | 18 | T25 a/b TDC/TDF | 1 | 81.0 lbs | 1/2 inch EMT | - | - | - | -
82 | 82 | 60 | 18 | T25 a/b TDC/TDF | 1 | 83.0 lbs | 1/2 inch EMT | - | - | - | -
84 | 84 | 60 | 18 | T25 a/b TDC/TDF | 1 | 85.0 lbs | 1/2 inch EMT | - | - | - | -
86 | 86 | 60 | 18 | T25 a/b TDC/TDF | 1 | 87.0 lbs | 1/2 inch EMT | - | - | - | -
88 | 88 | 60 | 18 | T25 a/b TDC/TDF | 1 | 89.0 lbs | 1/2 inch EMT | - | - | - | -
90 | 90 | 60 | 18 | T25 a/b TDC/TDF | 1 | 91.0 lbs | 1/2 inch EMT | - | - | - | -
92 | 92 | 60 | 18 | T25 a/b TDC/TDF | 1 | 94.0 lbs | 1/2 inch EMT | - | - | - | -
94 | 94 | 60 | 18 | T25 a/b TDC/TDF | 1 | 96.0 lbs | 1/2 inch EMT | - | - | - | -
96 | 96 | 60 | 18 | T25 a/b TDC/TDF | 1 | 98.0 lbs | 1/2 inch EMT | - | - | - | -
98 | 98 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 38.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
100 | 100 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 38.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
102 | 102 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 39.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
104 | 104 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 40.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
106 | 106 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 41.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
108 | 108 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 41.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
110 | 110 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 42.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
112 | 112 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 43.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
114 | 114 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 44.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
116 | 116 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 44.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
118 | 118 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 45.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle
120 | 120 | 60 | 18 | T25 a/b TDC/TDF | - | - | - | 46.0 lbs | 1/2 inch EMT | I | 2-1/2 x 1/8 Hot Rolled Angle

## Reinforcement
Length Breakpoints The length breakpoint table is for specifying the quantity of rods along the width and/or depth of duct, based on the length of that dimension. We can allocate a quantity on each position (Centrally and Externally). Only if the Stiffener have been set to Internal or Both for Central or End types would tie rods quantities be used based on this dialogue. Application of 1 central and 1 end would result in at least 3 tie rods as there would be at least 1 in the middle and at least 1 at each end of the duct.
<= Length | # Center Tie Rods | # End Tie Rods
42 | 0 | 0
96 | 1 | 0
120 | 0 | 1
Span Breakpoints The span breakpoints only apply when using internal based stiffening (Tie rods). The span of the tie rod (it's length) determines the type (diameter) of it. The length used is the opposite duct side length than was used to determine the number of tie rods in the 'Length' breakpoint table and it defines the rod & bolt types + hole diameter to cut for each tie rod. Although the number of tie rods is determined off the width, the type of tie rod is determined by the depth (and vice-versa...). As shown in the example cost breakdown above, Span breakpoints can be specified to allow for variant rod thicknesses and values to offset 2 rods when using vertical and horizontal rod placement. Based on the size, we can dictate the Hole diameter to be cut on the development for manufacture, and where to offset the holes from the edge of the duct.
<= Span | Tie Rod Hole Diameter | Central Tie Rod Offset (width) | Central Tie Rod Offset (depth) | Connector Tie Rod Offset (width) | Connector Tie Rod Offset (depth) | Tie Rod Extension | Tie Rods | Bolts | Qty per Tie Rod
36 | 0.3125 | -0.353 | 0.353 | 0.5 | 1.206 | 0 | 1/2 inch EMT | ConduLok 1/2 | 2
Electrical metallic tubing
|  |  |  | SIZE | (OD)
|  |  |  | 1/2 | 0.706
|  |  |  | 3/4 | 0.922
External Breakpoints When specified to use External stiffening, the External breakpoints become active and is where to specify the materials wanting to be used/costed for the stiffener.
<= LS | Material |  |  | Corners
96 | None |  |  | None
120 | 2-1/2 x 1/8 Hot Rolled Angle |  |  | None
Note: The contents of these tables can be copied and pasted into the Autodesk Fabrication specification.